## Changes
| Type | Attribute | Change
2023-12-20 | Substation | mRID | Made optional unless CIM LTDS data is being produced
| Substation | area | Description updated to align with license name or abbreviation
| Substation | name | Description changed to force alignment with existing LTDS naming
| Substation | voltages | Updated unit to kV
| Substation | demandFirmCapacity | demandTotalCapacity changed to demandFirmCapacity
| Substation | demandConnectedCapacity | Added a demandConnectedCapacity attribute
| Substation | demandContractedCapacity | Changed cardinality to optional
| Substation | demandAvailableCapacity | Updated documentation
| Substation | demandMaximum | Updated documentation
| Substation | demandMinimum | Updated documentation
| Substation | demandConstraintLimitingFactor | Updated documentation
| Substation | generationAvailabileCapacity | Updated documentation
| Substation | generationConnectedCapacity | Changed to optional
| Substation | generationContractedCapacity | Changed to optional
| Substation | generationConstraintLimitingFactor | Updated documentation
| Substation | breakerRatedCurrent | Changed to optional, updated unit to kA
| Substation | breakerBreakingCapacity | Changed to optional, updated unit to kA
| Substation | breakerMakingCapacity | Updated unit to kA
| Substation | breakerAvailableCapacity | Updated unit to kA
| Substation | breakerShortCircuitCurrent | Updated unit to kA
| Substation | Demands | Updated documentation
| Substation | Generators | Updated documentation
| Substation | Storage | Updated documentation
| Circuit |  | Updated documentation
| Circuit | mRID | Updated documentation
| Circuit | demandMaximum | Updated documentation
| Circuit | demandMinimum | Updated documentation
| Circuit | demand99Percentile | Updated documentation
| Circuit | demand75Percentile | Updated documentation
| Circuit | demand50Percentile | Updated documentation
| Circuit | demand25Percentile | Updated documentation
| Circuit | demandConnectedCapacity | Added a demandConnectedCapacity attribute
| Circuit | FromSubstation | Updated documentation
| Circuit | ToSubstation | Updated documentation and cardinality
| Circuit | Geometry | Changed to optional
| Demand |  | Updated documentation
| Demand | mRID | Updated documentation
| Demand | demandContractedCapacity | Changed cardinality to optional
| Generator | mRID | Updated documentation
| Generator | aggregate | Updated documentation
| Generator | voltage | Updated unit to kV
| Storage | mRID | Updated documentation
| Storage | aggregate | Updated documentation
| Storage | voltage | Updated unit to kV
| Transformer | mRID | Updated documentation
| Transformer | voltages | Updated unit to kV
| Rating | fromVoltage | Updated unit to kV
| Rating | toVoltage | Updated unit to kV
| Constraint |  | Updated documentation

## Substation
Element | Attribute Name | Attribute Type | Cardinality | Base Type | Description
Substation | A Substation with connect demand, generation or storage. A substation can be either a Grid Supply Point (GSP), Bulk Supply Point (BSP), Primary or Secondary station
Substation | mRID | Identifier | 0..1 | String | The Master Resource ID of the Substation. Where CIM data is being produced for LTDS this ID should be present, persistent across each release of the data and should be the same as the mRID/rdf:ID of the CIM Substation. If data is produced prior to the CIM LTDS data being published this attribute is optional.
Substation | type | Enum [GSP, BSP, Primary, Secondary] | 1..1 | String | The type of the substation
Substation | area | LicenseArea | 1..1 | String | The name of the license area. This may be the full text name or an abbreviation that should align with the abbreviations used in the license (e.g. Eastern Power Networks or EPN)
Substation | name | String | 1..1 | String | The human readable name of the substation. This should be consistent with the naming used in LTDS, either Tables 1-8 of existing Excel format, or CIM Substation names for the CIM LTDS data
Substation | description | String | 0..1 | String | Free text for any additional descriptive data about the substation
Substation | shortCode | String | 0..1 | String | Short code name for substation (alphanumeric, uppercase letters only)
Substation | voltages | kV | 1..n | Float | The voltages at the Substation in Kilovolts (kV)
Substation | longitude | DecimalDegrees | 1..1 | Float | The longitude value of the substation as a single latitude/longitude point. For a GeoJSON Heatmap format this data will be part of the feature itself allowing for more complex geometry
Substation | latitude | DecimalDegrees | 1..1 | Float | The latitude value of the substation as a single latitude/longitude point. For a GeoJSON Heatmap format this data will be part of the feature itself allowing for more complex geometry
Substation | Primary | Identifier | 0..1 | String | The identifier of the Primary this Substation is supplied by. It is assumed the corresponding Substation will be contained within the data. Optional as a GSP, BSP or Primary Substation will not have this reference
Substation | BSP | Identifier | 0..1 | String | The identifier of the BSP this Substation is supplied by. It is assumed the corresponding Substation will be contained within the data. Optional as a GSP or BSP Substation will not have this reference, and the Scottish networks do not have BSPs
Substation | GSP | Identifier | 0..1 | String | The name of the GSP this Substation is within. It is assumed the corresponding Substation will be contained within the data. Optional as a GSP Substation will not have this reference
Substation | demandFirmCapacity | MVA | 1..1 | Float | The firm capacity for demand at the substation. Any constraints that impact this capacity should be listed as individual constraints linked to the substation
Substation | demandConnectedCapacity | MVA | 0..1 |  | Sum of all demand currently connected at the substation. This includes individual demands and storage that are explicitly defined and aggregate value of other connect demands and storage. The value for demandConnectedCapacity must be greater than or equal to the sum of the demandConnectedCapacity values in the demand and Storage elements.
Substation | demandContractedCapacity | MVA | 0..1 | Float | Sum of all demand currently contracted at the substation which is not yet connected (i.e. do not include any demand that is included in demandConnectedCapacity). This includes individual demands and storage that are explicitly defined and aggregate value of other connect demands and storage. The value for demandContractedCapacity must be greater than or equal to the sum of the demandContractedCapacity values in the demand and Storage elements
Substation | demandQuotedCapacity | MVA | 0..1 | Float | Sum of all demand currently quoted at the substation excluding contracted and connected (i.e. does not include demandConnectedCapacity or demandContractedCapacity). This includes individual demands and storage that are explicitly defined and aggregate value of other connect demands and storage. The value for demandQuotedCapacity must be greater than or equal to the sum of the demandQuotedCapacity values in the demand and Storage elements
Substation | demandAvailableCapacity | MVA | 1..1 | Float | The available demand capacity at the substation. This value is calculated based on total firm capacity, maximum demand, connected capacity, quoted capacity, contracted capacity, and any other constraints on the network. The value should reflect the capacity a network operator would make available to a connecting party, which may be calcualted for the most onerous season, or a value based on more detailed analysis and internal policies
Substation | demandMaximum | MVA | 0..1 | Float | The maximum demand at the substation. This is a normalised value calculated using historic measured values during normal operating conditions .The data represents net demand corrected for any generation at the substation, demand diversity factors, and any other internal processing normally undertaken. All substations at 33kV and above must include demand data; for substations below 33kV, if corrected, net demand data is not available, the value should be omitted. Users wishing to see separate summer/winter peaks can obtain this from the LTDS data
Substation | demandMinimum | MVA | 0..1 | Float | The minimum demand at the substation. This is a normalised value calculated using historic measured values during normal operating conditions. The data represents net demand corrected for any generation at the substation, demand diversity factors, and any other internal processing normally undertaken. All substations at 33kV and above must include demand data; for substations below 33kV, if corrected, net demand data is not available, the value should be omitted. Users wishing to see separate summer/winter peaks can obtain this from the LTDS data
Substation | demand99Percentile | MVA | 0..1 | Float | The 99th percentile of demanding at the substation. This is a normalised value calculated using historic measured values during normal operating conditions. The data represents net demand corrected for any generation at the substation, demand diversity factors, and any other internal processing normally undertaken. All substations at 33kV and above must include demand data; for substations below 33kV, if corrected, net demand data is not available, the value should be omitted.
Substation | demand75Percentile | MVA | 0..1 | Float | The 75th percentile of demanding at the substation. This is a normalised value calculated using historic measured values during normal operating conditions. The data represents net demand corrected for any generation at the substation, demand diversity factors, and any other internal processing normally undertaken. All substations at 33kV and above must include demand data; for substations below 33kV, if corrected, net demand data is not available, the value should be omitted.
Substation | demand50Percentile | MVA | 0..1 | Float | The 50th percentile of demanding at the substation. This is a normalised value calculated using historic measured values during normal operating conditions. The data represents net demand corrected for any generation at the substation, demand diversity factors, and any other internal processing normally undertaken. All substations at 33kV and above must include demand data; for substations below 33kV, if corrected, net demand data is not available, the value should be omitted.
Substation | demand25Percentile | MVA | 0..1 | Float | The 25th percentile of demanding at the substation. This is a normalised value calculated using historic measured values during normal operating conditions. The data represents net demand corrected for any generation at the substation, demand diversity factors, and any other internal processing normally undertaken. All substations at 33kV and above must include demand data; for substations below 33kV, if corrected, net demand data is not available, the value should be omitted.
Substation | demandConstraint | Enum [Red, Amber, Green] | 1..1 | String | A RAG definition of the demand constraints at the substation. A utility should provide details on how this RAG status is calculated as part of the accompanying documentation
Substation | demandConstraintLimitingFactor | Enum [Thermal, Voltage, FaultLevel] | 1..1 | String | The limiting factor for demand constraints, either thermal, voltage or fault level for the demandConstraint value
Substation | generationFirmCapacity | MVA | 1..1 | Float | The total firm generation capacity of the substation. Any constraints that impact this capacity should be listed as individual constraints linked to the substation
Substation | generationConnectedCapacity | MVA | 0..1 | Float | Sum of all generation currently connected at the substation. This includes individual generation and storage that are explicitly defined and aggregate value of other connect generation and storage. The value forgenerationConnectedCapacity must be greater than or equal to the sum of the generationConnectedCapacity values in the Generator and Storage elements
Substation | generationContractedCapacity | MVA | 0..1 | Float | Sum of all generation currently contracted at the substation which is not yet connected (i.e. do not include any generation that is included in generationConnectedCapacity). This includes individual generation and storage that are explicitly defined and aggregate value of other connect generation and storage. The value for generationContractedCapacity must be greater than or equal to the sum of the generationContractedCapacity values in the Generator and Storage elements
Substation | generationQuotedCapacity | MVA | 0..1 | Float | Sum of all quoted currently generation at the substation excluding any that are already contracted or connected. This includes individual generation and storage that are explicitly defined and aggregate value of other connect generation and storage. The value for generationQuotedCapacity must be greater than or equal to the sum of the generationQuotedCapacity values in the Generator and Storage elements
Substation | generationAvailableCapacity | MVA | 1..1 | Float | Available generation capacity at the substation.This value is calculated based on total firm generation, capacity, demand, connected capacity, quoted capacity, contracted capacity, and any other constraints on the network
Substation | generationConstraint | Enum [Red, Amber, Green] | 1..1 | String | A RAG definition of the demand constraints at the substation. A utility should provide details on how this RAG status is calculated as part of the accompanying documentation
Substation | generationConstraintLimitingFactor | Enum [Thermal, Voltage, FaultLevel] | 1..1 | String | The limiting factor for generation constraints, either thermal or fault level for the generationConstraint value
Substation | breakerRatedCurrent | kA | 0..1 | Float | The rated normal current of the circuit breaker is the RMS value of the current with which the circuit breaker shall be able to carry continuously
Substation | breakerBreakingCapacity | kA | 0..1 | Float | The short-circuit current that the breakers are capable of breaking. It is expressed in KA RMS at contact separation
Substation | breakerMakingCapacity | kA | 0..1 | Float | The making current of the circuit breaker, when closed on a short circuit, is the peak value of the maximum current wave (including dc component) in the first cycle of the current after the circuit is closed by the circuit breaker
Substation | breakerAvailableCapacity | kA | 0..1 | Float | The available capacity of the circuit breaker
Substation | breakerShortCircuitCurrent | kA | 0..1 | Float | The short circuit current of a circuit breaker is the RMS value of current that a breaker can carry in a fully closed condition without damage, for the specified time interval under prescribed condition. These ratings are based on thermal limitation
Substation | breakerShortCircuitDuration | Seconds | 0..1 | Float | Specified time interval the Short Circuit Current can be carried for without damage
Substation | reversePowerFlowTotalCapacity | MVA | 1..1 | Float | The reverse capacity for the substation from lower to higher voltage levels. 0 if there are no reverse powerflow capabilities
Substation | reversePowerFlowAvailableCapacity | MVA | 1..1 | Float | The available reverse capacity for the substation from lower to higher voltage levels.
Linked References (see other data definitions)
Substation | embeddedCapacityRegister | Link (URL) | 0..1 | String | A URL to the embedded capacity register entry for this station
Substation | Demands | demand | 0..n | demand | The demands at the station covering connected, contracted and quoted. This data is optional and may aggregated into the substation attributes, but utilities may optionally provide details on individual demands.
Substation | Generators | Generator | 0..n | Generator | The generators at the station covering connected, contracted and quoted. This data is optional and may aggregated into the substation attributes, but utilities may optionally provide details on individual generators.
Substation | Storage | Storage | 0..n | Storage | The storage devices at the station covering connected, contracted and quoted. This data is optional and may aggregated into the substation attributes, but utilities may optionally provide details on individual storage devices
Substation | Transformers | Transformer | 0..n | Transformer | The transformers connected at the substation
Substation | OtherConstraints | Constraint | 0..n | Constraint | An additional constraint on the Substation.
Substation | Curtailments | Curtailment | 0..n | Curtailment | Curtailments at the Substation

## Circuit
Element | Attribute Name | Attribute Type | Cardinality | Base Type | Description
Circuit | A circuit representing a connection between substations. This could be an HV circuit between stations or a circuit feeding multiple secondary stations from a primary. This data element is provided to support utilities that wish to share specfic or all circuits.
Circuit | mRID | Identifier | 1..1 | String | The Master Resource ID of the Circuit. Where CIM data is being produced for LTDS this ID should be present, persistent across each release of the data and should be the same as the mRID/rdf:ID of the CIM elements. If data is produced prior to the CIM LTDS data being published this attribute is optional.
Circuit | name | String | 1..1 | String | The human readable name of the circuit
Circuit | description | String | 0..1 | String | Free text for any additional descriptive data about the circuit
Circuit | demandMaximum | MVA | 0..1 | Float | The maximum load on the circuit. This is a value calculated using historic measured values and would not necessarily be corrected for generation on the circuit and normal operating conditions. All circuits at 33kV and above must include demand data
Circuit | demandMinimum | MVA | 0..1 | Float | The minimum demand on the circuit. This is a value calculated using historic measured values and would not necessarily be corrected for generation on the circuit and normal operating conditions. All circuits at 33kV and above must include demand data.
Circuit | demand99Percentile | MVA | 0..1 | Float | The 99th percentile of demand on the circuit. This is a value calculated using historic measured values and would not necessarily be corrected for generation on the circuit and normal operating conditions. All circuits at 33kV and above must include demand data
Circuit | demand75Percentile | MVA | 0..1 | Float | The 75th percentile of demand on the circuit. This is a value calculated using historic measured values and would not necessarily be corrected for generation on the circuit and normal operating conditions. All circuits at 33kV and above must include demand data
Circuit | demand50Percentile | MVA | 0..1 | Float | The 50th percentile of demand on the circuit. This is a value calculated using historic measured values and would not necessarily be corrected for generation on the circuit and normal operating conditions. All circuits at 33kV and above must include demand data
Circuit | demand25Percentile | MVA | 0..1 | Float | The 25th percentile of demand on the circuit. This is a value calculated using historic measured values and would not necessarily be corrected for generation on the circuit and normal operating conditions. All circuits at 33kV and above must include demand data
Circuit | demandConstraint | Enum [Red, Amber, Green] | 1..1 | String | A RAG definition of the demand constraints on the circuit. A utility should provide details on how this RAG status is calculated
Circuit | demandConnectedCapacity | MVA | 0..1 | Float | Sum of all demand currently connected on the circuit
Circuit | demandContractedCapacity | MVA | 0..1 | Float | Sum of all demand currently contracted on the circuit which are not yet connected (i.e. do not include any demand that is included in demandConnectedCapacity).
Circuit | demandQuotedCapacity | MVA | 0..1 | Float | Sum of all demand currently quoted on the circuit excluding contracted and connected (i.e. does not include demandConnectedCapacity or demandContractedCapacity).
Circuit | demandAvailableCapacity | MVA | 0..1 | Float | The available demand capacity on the circuit. This value is calculated based on the circuit rating, maximum demand, contracted capacity, and any other constraints on the network
Circuit | summerRating | MVA | 0..1 | Float | Summer rating for minimum rated section in the circuit (i.e. limiting series element)
Circuit | winterRating | MVA | 0..1 | Float | Winter rating for minimum rated section in the circuit (i.e. limiting series element)
Circuit | voltage | KV | 1..1 | Float | Voltage of the circuit
Circuit | FromSubstation | Identifier | 1..1 | String | mRID of the Substation the Circuit is from (used where CIM data is being produced and the mRID attributes are populated for Substations). Where no CIM mRID is yet being produced, the name of the Substation should be used
Circuit | ToSubstation | Identifier | 0..n | String | mRID of the Substations the Circuit is to (optional if LV circuits are shown but no LV/Secondary substations). Where CIM data is being produced the identifiers attributes reflect the mRID of the Substations . Where no CIM mRID is yet being produced, the names of the Substations should be used
Circuit | Geometry | Geometry | 0..1 | Geometry | The geometry of the circuit
Circuit | OtherConstraints | Constraint | 0..n | Constraint | An additional constraint on the Circuit.
Geometry | The geometry of the line, this will be one or more Lines i.e. series of ordered coordinates. Multiple Lines allowed to allow for radial geometries. It is likely that this will be rendered as a GeoJSON geometry in that format
Geometry | type | String | 1..1 | String | The geometry type (LineString or MultiLineString)
Geometry | Lines | Line | 1..n | Line | The Line elements
Line | A series of coordinates
Line | Coordinates | Coordinate | 2..n | Coordinate | 2 or more coordinates for a line
Coordinate | A coordinate of latitude/longitude
Coordinate | longitude | DecimalDegrees | 1..1 | Float | The longitude value of the coordinate as a single latitude/longitude point. For a GeoJSON Heatmap format this data will be part of the LineString geometry
Coordinate | latitude | DecimalDegrees | 1..1 | Float | The latitude value of the coordinate as a single latitude/longitude point. For a GeoJSON Heatmap format this data will be part of the LineString geometry

## Demand
Element | Attribute Name | Attribute Type | Cardinality | Base Type | Description
Demand | Represents an individual or aggregated demand at the substation. This may represent the aggregation of all generation at a voltage level or individual connected/contracted/quoted generators
Demand | mRID | Identifier | 0..1 | String | The Master Resource ID of the demand. Where CIM data is being produced for LTDS this ID should be present, persistent across each release of the data and should be the same as the mRID/rdf:ID of the CIM elements. If data is produced prior to the CIM LTDS data being published this attribute is optional.
Demand | name | String | 1..1 | String | The human readable name of the demand
Demand | aggregate | Boolean | 1..1 | Boolean | True if the demand represents an aggregation of multiple demands all connected at a single voltage level
Demand | demandConnectedCapacity | MVA | 1..1 | Float | The currently connected demand capacity
Demand | demandContractedCapacity | MVA | 0..1 | Float | The currently contracted demand capacity which is not yet connected (i.e. do not include any demand that is included in demandConnectedCapacity)
Demand | demandQuotedCapacity | MVA | 0..1 | Float | The currently active quoted demand capacity excluding contracted and connected (this is optional as connected/contracted generation may not have records of quotes and after a value is contracted this value is no longer relevant)
Demand | voltage | KV | 1..1 | Float | The voltage the demand is connected at
Demand | technologyType | String | 0..1 | String | The technology the connected demand

## Generator
Element | Attribute Name | Attribute Type | Cardinality | Base Type | Description
Generator | Represents an individual or aggregated generator at the substation. This may represent the aggregation of all generation at a voltage level or individual connected/contracted/quoted generators
Generator | mRID | Identifier | 1..1 | String | The Master Resource ID of the Generator. Where CIM data is being produced for LTDS this ID should be present, persistent across each release of the data and should be the same as the mRID/rdf:ID of the CIM elements. If data is produced prior to the CIM LTDS data being published this attribute is optional.
Generator | name | String | 1..1 | String | The human readable name of the generator
Generator | aggregate | Boolean | 1..1 | Boolean | True if the generator represents an aggregation of multiple generators all connected at a single voltage level. If technologyType is left blank it is assumed that the Generator aggregates all generation types. If technologyType is populated and aggregate is true the Generator reflects the aggregate of that type of generation
Generator | generationConnectedCapacity | MVA | 1..1 | Float | The currently connected generation capacity
Generator | generationContractedCapacity | MVA | 1..1 | Float | The currently contracted generation capacity excluding any that are already contracted or connected (i.e. do not include any generation that is included in generationConnectedCapacity)
Generator | generationQuotedCapacity | MVA | 0..1 | Float | The currently active quoted generation capacity above contracted (this is optional as connected/contracted generation may not have records of quotes and after a value is contracted this value is no longer relevant)
Generator | voltage | kV | 1..1 | Float | The voltage the generator is connected at
Generator | technologyType | String | 0..1 | String | The technology the connected generation e.g. CHP, Wind, PV, Battery

## Storage
Element | Attribute Name | Attribute Type | Cardinality | Base Type | Description
Storage | Represents an individual or aggregated storage at the substation. This may represent the aggregation of all storage at a voltage level or individual connected/contracted/quoted storage
Storage | mRID | Identifier | 1..1 | String | The Master Resource ID of the Storage device. Where CIM data is being produced for LTDS this ID should be present, persistent across each release of the data and should be the same as the mRID/rdf:ID of the CIM elements. If data is produced prior to the CIM LTDS data being published this attribute is optional.
Storage | name | String | 1..1 | String | The human readable name of the storage device
Storage | aggregate | Boolean | 1..1 | Boolean | True if the generator represents an aggregation of multiple storage devices all connected at a single voltage level. If technologyType is left blank it is assumed that the Storage aggregates all storage types. If technologyType is populated and aggregate is true the Storage reflects the aggregate of that type of storage
Storage | demandConnectedCapacity | MVA | 1..1 | Float | The currently connected demand capacity
Storage | demandContractedCapacity | MVA | 1..1 | Float | The currently contracted demand capacity which is not yet connected (i.e. do not include any demand that is included in demandConnectedCapacity)
Storage | demandQuotedCapacity | MVA | 0..1 | Float | The currently active quoted demand capacity excluding contracted and connected (this is optional as connected/contracted generation may not have records of quotes and after a value is contracted this value is no longer relevant)
Storage | generationConnectedCapacity | MVA | 1..1 | Float | The currently connected generation capacity
Storage | generationContractedCapacity | MVA | 1..1 | Float | The currently contracted generation capacity excluding any that are already contracted or connected (i.e. do not include any generation that is included in generationConnectedCapacity)
Storage | generationQuotedCapacity | MVA | 0..1 | Float | The currently active quoted generation capacity above contracted (this is optional as connected/contracted generation may not have records of quotes and after a value is contracted this value is no longer relevant)
Storage | voltage | kV | 1..1 | Float | The voltage the storage is connected at
Storage | technologyType | String | 0..1 | String | The technology the connected generation e.g. PumpStorage, Battery

## Transformer
Element | Attribute Name | Attribute Type | Cardinality | Base Type | Description
Transformer | A transformer at a substation. Optional but can be useful if ratings and capacity are required on a per-transformer level
Transformer | mRID | Identity | 1..1 | String | mRID of the Substation the Transformer is within (used where CIM data is being produced and the mRID attributes are populated for Substations). Where no CIM mRID is yet being produced, the name of the Substation should be used
Transformer | name | String | 1..1 | String | The human readable name of the storage device
Transformer | voltages | kV | 2..3 | Float | The primary, secondary (and optional tertiary) voltages of the transformer
Transformer | Ratings | Rating | 0..n | Rating | The ratings of the transformer as defined by the Ratings element
Rating | A rating assigned to a transformer. This would allow multiple ratings to be defined for a single transformer e.g. OFAF ONAN and different ratings for different voltages (e.g. 11->33 is different from 33->11 for reverse powerflow)
Rating | name | String | 1..1 | String | Human readble name of the rating
Rating | summerRating | MVA | 1..1 | Float | Summer Rating in MVA
Rating | winterRating | MVA | 1..1 | Float | Winter Rating in MVA
Rating | fromVoltage | kV | 1..1 | Float | From voltage for the rating
Rating | toVoltage | kV | 1..1 | Float | To voltage for the rating

## Constraint
Element | Attribute Name | Attribute Type | Cardinality | Base Type | Description
Constraint | An additional constraint/restriction on the Substation or Circuit. This is intended for non-numeric constraints e.g. to denote physical restrictions on reinforcement
Constraint | name | String | 1..1 | String | Human readable name of the constraint
Constraint | description | String | 1..1 | String | Free text for any additional descriptive data about the constraint
Constraint | type | Enum [Voltage, Physical, Other] | 1..1 | String | The type of constraint (enumerated field to allow for easier processing/identification)

## Curtailment
Element | Attribute Name | Attribute Type | Cardinality | Base Type | Description
Curtailment | Curtailment of demand or generation capacity at the substation with optional day/time and season parameters
Curtailment | name | String | 1..1 | String | Human readable name of the curtailment
Curtailment | description | String | 1..1 | String | Free text for any additional descriptive data about the curtailment
Curtailment | type | Enum [Demand, Generation] | 1..1 | String | The type of curtailment (enumerated field to allow for easier processing/identification)
Curtailment | curtailedBy | MVA | 1..1 | Float | The amount the demand/generation capacity is curtailed by
Curtailment | technologyType | MVA | 0..1 | Float | The technology the curtailment applies to e.g for generation CHP, Wind, PV, Battery
Curtailment | season | Enum[Spring, Summer, Autumn, Winter] | 0..1 | String | The season this curtailment applies during
Curtailment | dayType | Enum[Weekday, Weekend] | 0..1 | String | The type of day the curtailment applies during (weekday or weekend)
Curtailment | startTime | Time (HH:mm:ss) | 0..1 | Time | The start time of a curtailment (inclusive)
Curtailment | endTime | Time (HH:mm:ss) | 0..1 | Time | The end time of a curtailment (exclusive)

## HeatmapDataSet
Element | Attribute Name | Attribute Type | Cardinality | Base Type | Description | URI
HeatmapDataSet | A single instance of a published dataset. The descriptions of these fields are taken from the Dublin Core Standard
HeatmapDataSet | contributor | String | 1..1 | String | An entity responsible for making contributions to the resource. | http://purl.org/dc/terms/contributor
HeatmapDataSet | coverage | String | 1..1 | String | The spatial or temporal topic of the resource, spatial applicability of the resource, or jurisdiction under which the resource is relevant. http://purl.org/dc/terms/coverage | http://purl.org/dc/terms/contributor
HeatmapDataSet | creator | String | 1..1 | String | An entity responsible for making the resource. | http://purl.org/dc/terms/creator
HeatmapDataSet | date | DateTime | 1..1 | DateTime | A point of time associated with an event in the lifecycle of the resource. For this implementation this will represent the date the data set is valid from | http://purl.org/dc/terms/date
HeatmapDataSet | description | String | 1..1 | String | An account of the resource. | http://purl.org/dc/terms/description
HeatmapDataSet | format | String | 1..1 | String | The file format of the resource | http://purl.org/dc/terms/format
HeatmapDataSet | identifier | String | 1..1 | String | An unambiguous reference to the resource within a given context. | http://purl.org/dc/terms/identifier
HeatmapDataSet | issued | DateTime | 1..1 | DateTime | Date of formal issuance of the resource. | http://purl.org/dc/terms/issued
HeatmapDataSet | language | String | 1..1 | String | A language of the resource. | http://purl.org/dc/terms/language
HeatmapDataSet | publisher | String | 1..1 | String | An entity responsible for making the resource available. | http://purl.org/dc/terms/publisher
HeatmapDataSet | rights | String | 1..1 | String | Information about rights held in and over the resource. | http://purl.org/dc/terms/rights
HeatmapDataSet | title | String | 1..1 | String | A name given to the resource. | http://purl.org/dc/terms/title
HeatmapDataSet | valid | DateTime | 2..2 | DateTime | A date range for the validity of a resource. This should be two dates to form a range. The first date is inclusive and the second date exclusive | http://purl.org/dc/terms/valid
HeatmapDataSet | Substations | Substation | 0..n | Substation | A list of substations with heatmap data
HeatmapDataSet | Circuits | Circuit | 0..n | Circuit | A list of circuits with heatmap data